## Slide 1
Smart Fire Fighting System
Suppression that doesn't wait on the network.
Graduation Project Defense · Modern Academy for Engineering & Technology · Supervisor: Dr. Maha Gaber

## Slide 2
AGENDA
This defense, in four moves.
01
Architecture
Two tiers, one bus
02
AI & Vision
Confirm, see, alert
03
Reliability & Results
Proven, measured
04
Live Demonstration
Ground truth

## Slide 3
SITUATION
Minutes
A structure fire becomes unsurvivable in minutes — hazard accumulates as t², not linearly.
Heat release ∝ t²

## Slide 4
COMPLICATION
Conventional detectors are single-signal and blind; “smart” ones depend on the very network a fire takes down.
LEGACY POINT DETECTION
— Single modality (smoke OR heat)
— Building-wide, no zone resolution
— No visual confirmation
CLOUD-SMART SYSTEMS
— AI lives in the cloud
— Round-trip latency in the loop
— Fails when the network fails

## Slide 5
QUESTION
So: how do you get AI-grade intelligence and a guaranteed local response?

## Slide 6
ANSWER · THE GOVERNING THESIS
A fail-operational,
AI-confirmed,
room-level fire system
that suppresses in one control cycle —
without waiting on the network.

## Slide 7
SYSTEM AT A GLANCE
Two tiers, one bus: deterministic edge control + probabilistic AI, decoupled by MQTT.
ESP32 CONTROL TIER Level-driven loop 9 servos · 4 pumps
Mosquitto MQTT 1883
AI PERCEPTION TIER YOLOv11 · CUDA FP16 fusion + occupancy
Telegram · sffs_bot
Node-RED Control Room
telemetry
command
image payload + sensor metrics

## Slide 8
CAPABILITY MAP
Four rooms, nine servos, four pumps — with occupancy-aware suppression that protects people first.
4
Rooms
9
Servos
4
Pumps
[ 4-Room Layout — figure pending ]
Instant Visual Alerting
real-time fire-zone image capture + metrics
DELIVERED
Occupancy-Aware Suppression
line-crossing head-count protects people first
DELIVERED
Face-Identity Rescue Tier
per-person identification for priority rescue
ROADMAP

## Slide 9
THE PYRAMID
Everything that follows defends three claims.
01
Zonal Autonomy
Per-room detection + isolation, independent of the broker.
02
AI-Confirmed Perception
Vision + multi-sensor fusion cuts false alarms and misses.
03
Engineered Reliability
Fail-operational, power-budgeted, edge-cached actuation.

## Slide 10
THE NUMBERS WE'LL PROVE
Hero metrics — measured on the deployment rig.
23 / 7
FPS GPU(RTX 3050) / CPU
4 / 9 / 4
Rooms / Servos / Pumps
~4.1 A
peak on 5V·5A (20% margin)
1 cycle
edge isolation latency
Visual ground-truth
image + metrics ≤ 1 alert cycle
ADC 2000
gas threshold (mid of 0–4095)

## Slide 11
01
PILLAR 1
Zonal Autonomy
Each room detects and suppresses for itself — independent of the network.

## Slide 12
SYSTEM AT A GLANCE
The architecture in one view: two decoupled tiers, one broker.
EDGE CONTROL TIER
ESP32-WROOM-32DA Level-driven loop 9 servos · 4 pumps Local fire predicate
Mosquitto MQTT 1883 v3.1.1
AI PERCEPTION TIER
YOLOv11 · CUDA FP16 Sensor/vision fusion Occupancy tracking Telegram alerting
Node-RED Control Room
Telegram · sffs_bot
telemetry (2s)
command (retain)
image payload + metrics

## Slide 13
EDGE TIER
The edge tier is a real-time deterministic controller.
ESP32 CONTROL CORE non-blocking loop
wifi_manager
auto-reconnect
sensors
ADC1 · EMA · DHT · SR04
mqtt_handler
LWT · backoff · JSON
actuators
PCA9685 · relays
failsafe
connectivity FSM

## Slide 14
PHYSICAL LAYER · ISOMETRIC
Nine servos, four pumps, four rooms — an isometric cutaway of the plant.
R1
R2
R3
R4
Gas valve (trunk)
Door servos ×4
Corridor barriers ×2
Window servos ×2 (R3/R4)
Room pumps ×4
Isometric extrusion via Shape.ThreeD (editable native shapes).

## Slide 15
CONTROL STACK · ISOMETRIC
Exploded view: how the control stack physically layers.
Actuators — 9 servos / 4 pumps
4-channel relay bank (opto-isolated)
PCA9685 PWM driver @0x40
ESP32-WROOM-32DA controller
5V / 5A power rail (20% margin)
Each plate is an independent, recolourable native shape (Shape.ThreeD extrusion).

## Slide 16
ACTUATION BUS
One PCA9685 bus orchestrates all nine actuators.
ESP32
PCA9685 I²C 0x40 · 50 Hz
400 kHz
ch0
Gas valve
ch1-4
Room doors
ch5-6
Corridors
ch7-8
Windows R3/R4
PWM math tick = 20 ms / 4096 ≈ 4.88 µs 0°→180° = count 102 → 491

## Slide 17
CONTROL LAW
Control is level-driven: outputs are a pure function of the present state.
Read sensors
evaluateZones()
ZoneCommand
memcmp gate
apply / skip
Hardware is written only when the recomputed command differs from the last applied command.

## Slide 18
ZONAL EVALUATION
Each room decides for itself: the zonal evaluation matrix.
Fireᵣ = Buttonᵣ ∨ ( gasᵣ > 2000 ∧ warm )
Room
Button
Gas > 2000
⇒ Fire
Room 1
0
512
—
Room 2
0
480
—
Room 3
0
2150
FIRE
Room 4
1
470
FIRE

## Slide 19
GLOBAL OVERRIDES
Two global overrides escalate the whole structure instantly.
IR flame (active-LOW)
MQTT state = "FIRE"
OR
Room 1
Room 2
Room 3
Room 4

## Slide 20
EDGE-CACHING · COMPOUND
Edge-caching: we write hardware only when the world actually changes.
ZoneCommand[t-1] [0,1,0,0,...]
ZoneCommand[t] [0,1,1,0,...]
memcmp
↑ bit changed
single I²C write → one servo moves
Identical commands → no write (anti-chatter). Only the changed channel is actuated.

## Slide 21
THE CORE THESIS · COMPOUND
Suppression completes before the network even hears about it.
MQ-6
ESP32
PCA/Relay
Broker
AI
Telegram
gas > 2000
ZoneCommand
valve/door/pump
1 control cycle
telemetry (≤2s)
sensor_data
alert + image
Local suppression (red) closes within one cycle; the network path (grey) only observes it afterwards.

## Slide 22
WATER SAFETY
Hysteresis keeps the pumps from ever running dry.
10% — cut pumps
20% — resume pumps
Pumpᵣ = Fireᵣ ∧ pumpsAllowed Below 10% → pumps inhibited (dry-run guard) At ≥ 20% → pumps re-enabled The deadband prevents relay chatter near the threshold.

## Slide 23
FAIL-OPERATIONAL
When the network drops, the system doesn't: the failsafe FSM.
NORMAL
DEGRADED
RECOVERY
The FSM classifies link health for telemetry only. The local fire predicate — gas, flame, button — keeps detecting and suppressing regardless of broker state. Connectivity loss degrades remote confirmation, never the suppression core.

## Slide 24
M2M CONTRACT
The contract: function-partitioned MQTT topics, structured JSON.
Topic
Dir
QoS
Retain
sffs/sensors/data
ESP32→all
0
no
sffs/system/status
AI→ESP32
1
yes
sffs/system/heartbeat
ESP32→AI
0
LWT
sffs/ai/detection
AI→NR
0
no
sffs/ai/people_count
AI→NR
0
no
[ JSON payload — drop code PNG here ]

## Slide 25
PILLAR 1 — CLOSED
Zonal autonomy, proven — now, can it see?
Level-driven
outputs are a pure function of state
Edge-cached
hardware writes only on real change
Fail-operational
suppression independent of the network
Next: the AI tier that confirms, sees, and alerts.

## Slide 26
02
PILLAR 2
AI-Confirmed Perception
The system doesn't just sense — it sees, confirms, and tells you.

## Slide 27
PERCEPTION LOOP
Capture → detect + track → fuse → alert.
Camera
YOLOv11
Occupancy
Decision Engine
MQTT / Telegram

## Slide 28
DETECTOR
YOLOv11 runs dual-mode: CUDA FP16 on GPU, ONNX on CPU.
frame
letterbox 640
FP16 tensor
forward
NMS @ IoU 0.20
boxes
Acceptance gates: conf ≥ 0.50 (fire) · conf ≥ 0.75 (smoke) detect() never mutates the frame — draw() is a single final pass (clean frame for both models) GPU: every frame · CPU: fire inference every 3rd frame (tracking stays every frame)

## Slide 29
SNAPSHOT PIPELINE
The moment of detection becomes ground truth.
YOLOv11 confirms flame/smoke
capture affected-room frame
save detected_fires/alert_<ts>.jpg
dispatch to Telegram (non-blocking)
The saved frame is the exact image transmitted — on-screen detection and mobile alert are identical.
detected_fires\alert_20260619-001311-916843.jpg

## Slide 30
INSTANT VISUAL ALERTING
Image + metrics on the responder's phone.
photos\telegram masseg.png
State · confidence · source
Occupancy count (rescue priority)
Key sensor metrics (gas / temp)
Annotated detection image
AlertGate — 45 s cooldown per severity · escalation BYPASSES the cooldown (worsening event never silenced) · return to SAFE resets the high-water mark

## Slide 31
EDGE BENCHMARK
Real-time on the edge: 23 FPS GPU, 7 FPS CPU.
23 FPS
GPU · RTX 3050 (FP16)
7 FPS
CPU (ONNX, every 3rd)
GPU — fire case
CPU — safe case

## Slide 32
DUAL-MODE VISION
Count everyone, identify no-one — yet.
Line-Crossing Headcount
DELIVERED
Persistent-ID person tracking; a vertical boundary at x = 300 yields a live, directional occupancy count that feeds rescue-priority alerts.
Face-Identity Layer
ROADMAP
A designed extension: per-person identification to drive named priority-rescue alerts. Deferred on privacy and compute grounds.

## Slide 33
OCCUPANCY · DELIVERED
Occupancy by line-crossing: persistent tracks across x = 300.
x = 300
OUTSIDE
INSIDE
inside_count
+1
model.track(persist=True, classes=[0]) center_x > 300 = inside side change ⇒ ±1 (floored at 0)

## Slide 34
ROADMAP
A face-identity tier for priority rescue.
ROADMAP — designed, not yet implemented
face embeddings
match known occupants
named priority-rescue alert
Deferred deliberately: identity adds privacy obligations and compute load. The delivered occupancy count already enables rescue prioritisation without identifying anyone.

## Slide 35
FUSION
Sensors and vision agree before the structure escalates.
Source
State
Conf.
Manual override
FIRE
1.00
Gas / Flame / Camera (single)
FIRE
0.92
Multiple sources agree
FIRE
0.98
Temperature only
SENSOR_ALERT
0.65
None
SAFE
—
Asymmetric debounce: escalate immediately (safety first); de-escalate only after a 5 s cooldown.

## Slide 36
OCCUPANCY-AWARE
Alert prioritisation today, suppression modulation next.
Occupancy-Aware Alerting
DELIVERED
The live head-count is embedded in the Telegram alert, raising rescue priority when people remain inside an active hazard zone.
Occupancy-Modulated Suppression
ROADMAP
A planned extension in which actuation adapts to protect occupants (e.g. holding an egress path). Not yet wired into the ESP32 control law.

## Slide 37
LIVE DEMONSTRATION
From detection to suppression — in front of you.
photos\running_cv_model.png
Fallback demo video — insert .mp4
1 · induce gas in a room → local suppression fires
2 · present flame → global override
3 · show YOLO confirmation + snapshot → Telegram
4 · dashboard mirrors every state live
LIVE

## Slide 38
03
PILLAR 3
Validation & Experimental Results
Claims are only as good as the bench that proves them.

## Slide 39
LATENCY BREAKDOWN
Where the milliseconds go: suppression is the fast path.
Local edge → actuation
~15 ms
GPU YOLOv11 inference
~43 ms (23 FPS)
Telegram remote alert
~1–3 s (network)
one control cycle
Network lane compressed for scale. Local suppression completes far ahead of — and is never gated by — the remote alert.

## Slide 40
FALSE-ALARM MITIGATION
Tighter gates: fewer false alarms, no missed fire.
0.50
0.68
fire confidence
0.75
0.82
smoke confidence
Gas: EMA α = 0.15 + 60 s warm-up + ADC ≥ 2000 gate
Fusion: OR-gate needs a real sensor/vision signal
Temperature alone → soft SENSOR_ALERT (never FIRE)
Stability: 5 s de-escalation debounce + 45 s alert cooldown

## Slide 41
ZONAL ACTUATION · OPTION A
Validated on the maquette: the right zone, every time.
Zone
Sensor
Trigger
Actuation
Room 1
MQ-7 (CO)
> 2000 / button
valve+door+pump 1
Room 2
MQ-6 (LPG)
> 2000 / button
door+pump 2
Room 3
MQ-5 (CH4)
> 2000 / button
door+window+pump 3
Room 4
MQ-2 (smoke)
> 2000 / button
door+window+pump 4
cross-zone isolation ✓
R1
R2
R3
R4
Water hysteresis (cut < 10% / resume ≥ 20%) confirmed under live pump load.

## Slide 42
CONTRIBUTIONS
A modular, real-time, multi-agent fire platform.
Architectural modularity
Decoupled edge / perception tiers over MQTT — each independently restartable.
Real-time multi-agent sync
Deterministic ESP32 + probabilistic AI fused without blocking the control loop.
Fail-operational autonomy
Room-level detection and suppression independent of network and vision.
Dissemination
Paper-submission framework targeting IJADT.

## Slide 43
CONSTRAINTS
Honest constraints: where the current design stops.
Edge-compute thermal throttling
sustained GPU inference bounds the RTX 3050 clock under load
Static camera FOV
single fixed view; out-of-frame ignition relies on the independent sensor path
Remote-alert network dependency
Telegram delivery needs IP connectivity — suppression does not
Scope bounds
occupancy is a count, not an identity; thresholds are ADC-domain, not ppm-calibrated

## Slide 44
FUTURE VISION
From roadmap to active development.
ROADMAP
Face-Identity tier
ACTIVE DEVELOPMENT
named priority-rescue alerts (privacy + compute design)
ROADMAP
Occupancy-modulated suppression
ACTIVE DEVELOPMENT
actuation that protects egress and occupants
Platform extensions: MQTT-SN clustering · LoRaWAN fallback · TensorRT INT8 quantization

## Slide 45
CONCLUSION
A fail-operational,
AI-confirmed,
room-level fire system that suppresses
in one control cycle — without waiting on the network.
Zonal Autonomy
AI-Confirmed Perception
Engineered Reliability

## Slide 46
Thank you.
Questions & committee discussion.
Two-tier system
Zonal plant
Edge control loop
AI pipeline
Snapshot → Telegram
Results

## Slide 47
APPENDIX A · BACKUP
Hardware & electrical reference.
Item
Value
MCU
ESP32-WROOM-32DA (LX6 dual-core, 240 MHz)
Gas (ADC1)
R1 GPIO35 MQ-7 / R2 34 MQ-6 / R3 33 MQ-5 / R4 32 MQ-2
Gas threshold
ADC 2000 (mid of 0–4095) · EMA α 0.15 · 60 s warm-up
Actuation
PCA9685 @0x40, 50 Hz · 9 servos · 4 relay pumps (active-LOW)
Flame / DHT22
GPIO27 active-LOW / GPIO26 one-wire
Water (HC-SR04)
TRIG 15 / ECHO 36 · cut < 10% resume ≥ 20%
Power budget
~4.1 A peak on 5 V / 5 A (20% margin)

## Slide 48
APPENDIX B · BACKUP
Software & AI reference.
Item
Value
Vision
YOLOv11-nano best_nano_111.pt · CUDA FP16 · imgsz 640 · IoU 0.20
Confidence
fire 0.68 · smoke 0.82
Throughput
23 FPS GPU (RTX 3050) / 7 FPS CPU (ONNX, every 3rd frame)
Occupancy
yolo11n person track · line x = 300 · directional count
Fusion
manual 1.00 / gas|flame|cam 0.92 / multi 0.98 / temp 0.65
Alerting
Telegram sffs_bot · 45 s cooldown · escalation bypass
Resilience
edge predicate broker-independent · failsafe FSM · MQTT LWT